## CAPA status
Previous CAPA Completion status
Equipment Classification |  |  | String Inverter | Previous CAPA Completion status |  |  | 100%
Sr. No. | Equipment Classification | Sub component | CAPA | Status | Target Date of Completion | Supportings Link (Photos/ppt/pdf with time stamp) | Remarks | 20
1 | String Inverter | All make inverter | Change the damaged gasket of string inverter. | Not Applicable
2 | String Inverter | All make inverter | Change the paper membrane with SS membrane in string inverter. | Not Applicable
3 | String Inverter | All make inverter | Sealed the cable entry or minor access gape of the inverter. | Completed
4 | String Inverter | All make inverter | Silica gel [Montmorillomite Desiccant, Hygroscopic type] (Do not use dehumidification type) packets to be kept inside inverter | Not Applicable
5 | String Inverter | All make inverter | Spread natural chips pebbles below inverter to prevent grass growth and humidity. | In Practice
6 | String Inverter | All make inverter | Use Ant repellent chalk/gel on inverter door and at cable termination. | Completed
7 | String Inverter | All make inverter | Tightness of Earthing Cable for Inverter cabinet‐both end | Completed
8 | String Inverter | All make inverter | Grass level should not be exceeded more than approx. 200mm below string inverter. | Completed
9 | String Inverter | All make inverter | Ensure & Verify DC voltage of all 8 Strings (Vdc) | Completed |  |  | Checked all String Amps
10 | String Inverter | All make inverter | Replace the inverter incase of internal burning | Completed |  |  | INV Replaced
11 | String Inverter | All make inverter | Ensure & Verify Temperature of AC Cable Termination | Completed
12 | String Inverter | All make inverter | Visual inspection of Heat Sink, any dirt or cable touch | Completed
13 | String Inverter | All make inverter | Ensure ventilation and colling system of inverter/Inverter room | Completed
14 | String Inverter | All make inverter | Replace the identified faulty/damaged part. | Completed |  |  | INV Replaced
15 | String Inverter | All make inverter | Ensure the functionality of the replaced part | Completed |  |  | INV Replaced
16 | String Inverter | All make inverter | Ensure communication ,alarm and events record. | Completed
17 | String Inverter | All make inverter | Ensure SMPS voltage | Not Applicable
18 | String Inverter | All make inverter | Ensure Grid voltage | Completed
19 | String Inverter | All make inverter | Ensure fresh air requirement of inverter room is as per OEM recommendation | Not Applicable
20 | String Inverter | All make inverter | Ensure the protection parameter and grid parameter as per Grid code | Completed

## Master CAPA Sheet (hidden)
Sr No: | Area | Equipment Classification | Sub component | Capa
1 | AC HT Cable | HT Cable | Boot kit | Ensure Boot kits used in RMU with proper rating. | 1HT Cable
2 | AC HT Cable | HT Cable | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. | 2HT Cable
3 | AC HT Cable | HT Cable | Busbar | Ensure HV insulation tape should be provided in all open areas in the bus bar. | 3HT Cable
4 | AC HT Cable | HT Cable | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 4HT Cable
5 | AC HT Cable | HT Cable | Cable Support | Ensure Installation of proper cable support. | 5HT Cable
6 | AC HT Cable | HT Cable | Cable tray | Ensure Metallic cable tray is replaced with insulated type cable tray. HT tape also used to wrap the metallic cable tray. | 6HT Cable
7 | AC HT Cable | HT Cable | Cable tray | Ensure packing of insulation is placed between metallic trefoil clamp and HT cable laid over tray to avoid cutting of insulation with metallic edges of clamp. | 7HT Cable
8 | AC HT Cable | HT Cable | Cable tray | Ensure that grass below cable tray is removed | 8HT Cable
9 | AC HT Cable | HT Cable | Control Cable | Ensure tightness of all Power and Control cable connections.Ensure Tightness is being done using torque wrench as per defined torque by OEM. | 9HT Cable
10 | AC HT Cable | HT Cable | HT Cable | Ensure HT termination is covered with HT tape/ Terminal cover to provide additional insulation. | 10HT Cable
11 | AC HT Cable | HT Cable | HT Cable | Ensure cable IR Value is measured and recorded. End termination kits of Cables with low IR values need to be checked physically and to be replaced if required.And click picture of equipment/termination/joint during PM & same need to be uploaded on SAP. | 11HT Cable
12 | AC HT Cable | HT Cable | HT Cable | Ensure Cables, boots, joints should be cleaned regularly to prevent partial discharge failure. | 12HT Cable
13 | AC HT Cable | HT Cable | HT Cable | Ensure checking of Control/Power Cable near gland area for any damages. | 13HT Cable
14 | AC HT Cable | HT Cable | HT Cable | Ensure connection of cable braid with earth bar of panel. | 14HT Cable
15 | AC HT Cable | HT Cable | HT Cable | Ensure Only Raychem/3M make kits is used for jointing work, Ensure that procedure of Jointing/Termination followed is as per OEM manual. Also, ensure Jointing work is performed by a certified jointer only. Need to restore end termination/joint through locally if certified vendor is not available immediately, and same need to re-terminated/re-jointed with authorized vendor as soon as possible. | 15HT Cable
16 | AC HT Cable | HT Cable | HT Cable | Ensure proper Bending radius of all end termination kits.it must be Single Core 25 X D - “D” means the overall diameter of the completed cable. | 16HT Cable
17 | AC HT Cable | HT Cable | HT Cable | Ensure Rain water/Moisture should not be in contact with cable joints/boots. | 17HT Cable
18 | AC HT Cable | HT Cable | HT Cable | Ensure RMU loop cables to be kept in charge condition by keeeping isolated from one end. | 18HT Cable
19 | AC HT Cable | HT Cable | HT Cable | Ensure Spare loop is prepared and laid between Power transformer and Outgoing panel to reduce MTTR in case of end termination failure of either side. Ensure Spare loop is prepared between IDT and RMU/ODU with both ends terminated and kept in store to reduce MTTR. | 19HT Cable
20 | AC HT Cable | HT Cable | HT Cable | Ensure Straight Through joints are laid on above ground to minimize further failure due to water ingress wherever feasible. | 20HT Cable
21 | AC HT Cable | HT Cable | HT Cable | Ensure the cable armor earthing is near to source earthing i.e. near the PSS end at Panel (ICT) (Single-end earthing) OR at both ends of cable between panel to panel. | 21HT Cable
22 | AC HT Cable | HT Cable | HT Cable | Ensure the cable clamping takes the weight of the cable and no mechanical load is exerted on busbar. Also, ensure the tightening of mounting hardware as recommended. | 22HT Cable
23 | AC HT Cable | HT Cable | HT Cable | Ensure the cable is properly fastened using non-metallic clamps. | 23HT Cable
24 | AC HT Cable | HT Cable | HT Cable | Ensure use of extra sleeve on both side of straight through joints where failure due to moisture ingress is high. | 24HT Cable
25 | AC HT Cable | HT Cable | Panel | Ensure Insulating paint is applied in HV Cable box of IDT/Aux transformer,Outdoor panels and Switchgear. | 25HT Cable
26 | AC HT Cable | HT Cable | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on immediate basis. Same to be ensure on quarterly basis. | 26HT Cable
27 | AC HT Cable | HT Cable | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside IDT HV Box/panel and proper sealing of HT-LT panel, transformer LV/HV cable box to be ensured to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 27HT Cable
0 | All Equipment |  | All Equipment | Liabilities should be closed | 0
0 | All Equipment |  | Earthing | Check earthing between earth rod and earth pit only after isolating the earthed equipment | 0
0 | Cable/Junction Box |  |  | Silicon sealant to be used for sealing of JB's. | 0
1 | DC Cable | DC Cable | Cable | Ensuring anti rodent cable will be laid at time of rectification. | 1DC Cable
2 | DC Cable | DC Cable | Cable | Ensuring cable will be laid in separate conduit at time of fault. | 2DC Cable
3 | DC Cable | DC Cable | DC String | Identify the Rat menace area and apply anti rodent chemical on frequent basis. If the rat menace area within a room then it can be easily implemented but for large scale(in acres) area it is difficult to implement effectively. | 3DC Cable
4 | DC Cable | DC Cable | DC String | Installing protector strip at identified sharp edges of purlin or parts of MMS | 4DC Cable
5 | DC Cable | DC Cable | DC String | Once crimping and fixing of connector done, connect the male and female MC4/Y connector, make sure a click sound is observed confirming connector are secured tightly. | 5DC Cable
6 | DC Cable | DC Cable | DC String | Physically Verify all the MC4/Y connector/Y connector connector tightness by gently pulling the connectors apart in no load condition. | 6DC Cable
7 | DC Cable | DC Cable | DC String | Puff sealant to be applied at conduit & conduit end to bend to avoid water ingress in the conduit. | 7DC Cable
8 | DC Cable | DC Cable | DC String | To replace damaged and broken DWC conduit with HDPE/DWC continuous pipe for underground cabling. | 8DC Cable
9 | DC Cable | DC Cable | DC String | To take care DC cable during table tilting work that there should not be stress on MC4/Y connector/Y connector connector. | 9DC Cable
10 | DC Cable | DC Cable | DC String | Use Key provided with MC4/Y connector/Y connector connectors to tighten the connectors and make sure they are fully tight with zero or at most one thread visible. | 10DC Cable
11 | DC Cable | DC Cable | DC String | Use proper crimping tool as per cable and lug size to crimp and once done do a pull out check to cross verify the integrity of the crimping done as loose crimping may lead to short circuit or heating in MC4/Y connector/Y connector connector. If tool became inferior then replace it. | 11DC Cable
12 | DC Cable | DC Cable | DC String | Restriction of vehicle movements & frequesnt grass cutting in dense growth areas. | 12DC Cable
13 | DC Cable | DC Cable | DC String | Restrict Cattle/sheep/any animal entry inside the plant premisis. | 13DC Cable
14 | DC Cable | DC Cable | DC String | Monitoring thermal imaging of all cable termination quarterly basis. | 14DC Cable
15 | DC Cable | DC Cable | DC String | Separate laying of Positive & Negative DC cables. | 15DC Cable
16 | DC Cable | DC Cable | DC String | DC Cable laid over the ground to be embeded inside the ground at -300mm level at pitch crossing at 10 MW | 16DC Cable
17 | DC Cable | DC Cable | DC String | MC4/Y connector should not be laid in pelin grip. | 17DC Cable
18 | DC Cable | DC Cable | DC String | Routine Thermography of branch connectors. | 18DC Cable
19 | DC Cable | DC Cable | MC4/Y connector | Avoid string connection in hanging position. Ensure cable laying and MC4/Y connector/Y connector / Y connection as per SOP. | 19DC Cable
1 | IDT | IDT | Bus duct | Ensure silica gel quality of bus duct (NSPBD/SPBD) breather and also ensure breather is sealed properly & breathing process through silica breather only. | 1IDT
2 | IDT | IDT | Busbar | Ensure additional support to be provided to LV Busbar from top side if existing support is not adequate. Also, ensure Installation of proper cable support at HV side if applicable. | 2IDT
3 | IDT | IDT | Busbar | Ensure Bimetallic strip to be used where copper and aluminum are connected with each other, and Stainless steel bolt must be used for connection if existing found corroded. | 3IDT
4 | IDT | IDT | Bushing | Ensure healthiness of LV bushing, if any crack observed over epoxy of bushing replace it immediately and maintain record of it. | 4IDT
5 | IDT | IDT | Bushing | Cork type gasket to be used in LV bushing | 5IDT
6 | IDT | IDT | Cable Box | Ensure during checking of cable box, if any insulator found over heated, cracked or miss aligned must be replaced with new one. | 6IDT
7 | IDT | IDT | Cable Box | Ensure Insulating paint to be applied in HV & LV Cable box busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 7IDT
8 | IDT | IDT | Cable box | Ensure no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque to ensure assembly fitments. | 8IDT
9 | IDT | IDT | Cable box | Ensure Phase to Phase separation sheet to be used where ever phase to phase clearance is not as per standerd in transformer hv and lv side. | 9IDT
10 | IDT | IDT | Cable box | Ensure Proper sealing of all cable box to ensure IP protection with door gaskets and cable entries. | 10IDT
11 | IDT | IDT | Cable box | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 11IDT
12 | IDT | IDT | Cable box | Ensure thermography of LV box to be done quarterly and need to be compare with other IDT. | 12IDT
13 | IDT | IDT | Cable box | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 13IDT
14 | IDT | IDT | Cable tray | Ensure LV cables to be properly laid on cable tray with trefoil formation and distance between trefoil to be maintain to avoid induction and leakage current. Also, ensure & check effective earthing of cable trays throughout the length. | 14IDT
15 | IDT | IDT | Control Cable | Ensure cable are having proper cable glands at cable entry point of Buchholz, PRV and MOG. | 15IDT
16 | IDT | IDT | Control Cable | Ensure cable from IDT to HT Panel panel used for protection tripping is armour cable. | 16IDT
17 | IDT | IDT | Control Cable | Validate IR value of relay contacts and control cables used for protection (PRV, MOG, Buchholz, WTI, OTI etc.) also ensure tightness of Control cable connections and provide record. Also, verify PRV and Bucholz relay switch rating with its name plate details. | 17IDT
18 | IDT | IDT | Coolling fan | Ensure cooling fan installation If repowering/overloading is above 135% of its capacity and ensure its running status availability in SCADA. | 18IDT
19 | IDT | IDT | Earthing | Ensure healthiness of earthing resistance measurement and maintain record. | 19IDT
20 | IDT | IDT | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 20IDT
21 | IDT | IDT | IDT | Ensure any deposition of oil & dust over Junction Box, Cable box and over tank surface to be properly cleaned. | 21IDT
22 | IDT | IDT | IDT | Ensure LV current measurement & thermography to be done on quarterly basis and maintain record of it. | 22IDT
23 | IDT | IDT | IDT | Transformer routine test to be performed and test results to be matched with FAT report. | 23IDT
24 | IDT | IDT | Junction box | Ensure Magic gel application at all JBs (Side-mounted PRV of JB,Buchholz,etc), and need to perform protection simulation of PRV & Buchholz through actual operation after application of magic gel & before charging. | 24IDT
25 | IDT | IDT | Mechanical Protection | Ensure and verify mechanical protection (WTI, OTI, PRV, Buchholz, MOG, OSR etc.) simulation at Filed/Local panel & at SCADA. Also, verify SCADA data for reporting of alarms & trippings | 25IDT
26 | IDT | IDT | NIFPS | Ensure Transformer NIFPS NRV/TCIV valve handle tied with cable tie or locked in service position. | 26IDT
27 | IDT | IDT | Oil | Ensure oil spillage to be cleared immediately from all the affected areas during oil top-up activity and while releasing air from transformer, | 27IDT
28 | IDT | IDT | Oil | Oil level in transformer should be between 30 deg. & ½ indication in Magnetic Oil Gauge(MOG) when the ambient temperature is 30 deg. Celsius. | 28IDT
29 | IDT | IDT | OTI-WTI | Ensure healthiness of WTI & OTI transducer and verify temperature readings at Local and in SCADA. | 29IDT
30 | IDT | IDT | OTI-WTI | Ensure WTI-OTI settings must be as per OEM recomendation. | 30IDT
31 | IDT | IDT | Power cable | Ensure healthiness of Power cables by checking IR values. | 31IDT
32 | IDT | IDT | Valve | Ensure apply lock on oil drain valve of IDT to prevent oil theft where ever oil theft cases observed. | 32IDT
1 | Internal Transmission Line | Internal Transmission line | Internal Transmission line | Ensure Barbed wire is wound by installing angle on Pole for extra protection from animal(Monkey). | 1Internal Transmission line
2 | Internal Transmission Line | Internal Transmission line | Internal Transmission line | Ensure Bird protection guard is installed at every poles. | 2Internal Transmission line
3 | Internal transmission line | Internal Transmission line | Internal transmission line | Ensure Conductor(4-5 mtr)near jumper area is covered with HT paint/ HT sleeve. | 3Internal Transmission line
4 | Internal transmission line | Internal Transmission line | Internal transmission line | Ensure that lugs used for both sides(Cable and Jumber) should be of same size for proper surface contact to avoid local heating. | 4Internal Transmission line
5 | Internal transmission line | Internal Transmission line | Internal Transmission line | Ensure HDPE pipe is installed at T-joint at every pole along with HT tape. | 5Internal Transmission line
6 | Internal transmission line | Internal Transmission line | Internal Transmission line | Thermography to be carried out on quarterly basis during peak time and Necessary corrective actions to be taken if temperature increases than permissible limits allowed in standards. | 6Internal Transmission line
7 | Internal transmission line | Internal transmission line | Internal transmission line | Ensure clearance between transmission line conductor and earth wire as per applicable standard. Also ensure proper binding & twisting of earth wire on tower with no rusting at the contact area. | 7Internal transmission line
8 | Internal transmission line | Internal Transmission line | Jumper | Ensure Proper tightness between lug and jumper at all the locations. Also Ensure proper Connection tightness with Jumpers to LA. | 8Internal Transmission line
9 | Internal transmission line | Internal Transmission line | LA | Earthing values of all LA as well as other equipments of plant to be checked for its healthiness and record to be maintained.Additional earth pit need to be installed where Earthing resistance value is >1 ohm.Ensure LA earthing continuty between LA and its earthpit. | 9Internal Transmission line
10 | Internal transmission line | Internal Transmission line | LA | Ensure Insulator base used for LA mounting is removed where LA counter is not installed. | 10Internal Transmission line
11 | Internal transmission line | Internal Transmission line | LA | Ensure measurement of IR values of LA, monitor LA counter and mA. | 11Internal Transmission line
12 | Internal transmission line | Internal Transmission line | LA | Ensure porcelain type LA is replaced with polymeric type where failure rate higher. | 12Internal Transmission line
13 | Internal transmission line | Internal Transmission line | LA | Ensure Proper sealing of outdoor-LA top cover with silicon sealant to prevent moisture ingress. Also, ensure proper jumper connections near LA. | 13Internal Transmission line
14 | Internal Transmission Line | Internal Transmission line | LA | Ensure Providing LA/ Surge arrester at both terminating ends of transmission lines having separate earth pit connection. | 14Internal Transmission line
15 | Internal transmission line | Internal Transmission line | LA | Ensure a Separate riser connection(Earthing strip) is installed/run from LA to Earthing pit with minimum nos of joints. | 15Internal Transmission line
16 | Internal transmission line | Internal Transmission line | LA | Visual inspection should be done and If any cracks/ deformation observed at base and top plate, such LAs to be replaced. | 16Internal Transmission line
1 | Inverter | Central Inverter | ABB inverter | Installation of polycarbonate sheets on identified bare busbars of ABB inverter | 1Central Inverter
2 | Inverter | Central Inverter | ABB inverter | Ensure cleaniliness of contactors K18,K19,K20 | 2Central Inverter
3 | Inverter | Central Inverter | All make inverter | Ensure the grounding connectivity of the inverter. | 3Central Inverter
4 | Inverter | Central Inverter | All make inverter | SPD healthiness routine check up. | 4Central Inverter
5 | Inverter | Central Inverter | All make inverter | Ensure earthpit connectivity with ground and inverter. | 5Central Inverter
6 | Inverter | Central Inverter | All make inverter | Periodic measurement of earth resistance. | 6Central Inverter
7 | Inverter | Central Inverter | All make inverter | Reduce the setting of hygrostat at 65% during rainy season. | 7Central Inverter
8 | Inverter | Central Inverter | All make inverter | Inspection of connectors and Performing routine preventive maintenance . Also Ensure & Verify SMPS volatge and feedback cables tightness. | 8Central Inverter
9 | Inverter | Central Inverter | All make inverter | Reduced the delay in two breaker and set 1 sec delay in two inverter for wake up after grid restoration. | 9Central Inverter
10 | Inverter | Central Inverter | All make inverter | Ensure & Verifying of CRM value of DC breaker/Isolator and AC breaker. | 10Central Inverter
11 | Inverter | Central Inverter | All make inverter | Tightness of the cable and cleanliness is to ensured time to time which can result in reduction of MTTR. | 11Central Inverter
12 | Inverter | Central Inverter | All make inverter | Increase the insulation detection threshold setting in Hitachi inverter. | 12Central Inverter
13 | Inverter | Central Inverter | All make inverter | Cleaning of the inverter filters on regular basis | 13Central Inverter
14 | Inverter | Central Inverter | All make inverter | Ensure & Verify any sign of decolourization at lugs/PCB/bus bars etc and must be fixed on immidiate basis | 14Central Inverter
15 | Inverter | Central Inverter | All make inverter | Ensure & Verify the condition of cables where armour cutting work done earlier. | 15Central Inverter
16 | Inverter | Central Inverter | All make inverter | Ensure & Verify tightness of all hardware on cover of cabinet(internal and outer side) | 16Central Inverter
17 | Inverter | Central Inverter | All make inverter | Ensure & Verify all connectors of PSFB card properly | 17Central Inverter
18 | Inverter | Central Inverter | All make inverter | Ensure & Verify for any electrolyte leakage or bulging in the AC capacitor | 18Central Inverter
19 | Inverter | Central Inverter | All make inverter | Ensure & Verify the temperature for DC breaker bus bars & IGBT Stacks heat sink. | 19Central Inverter
20 | Inverter | Central Inverter | All make inverter | Date & time reset after auxiliary fail | 20Central Inverter
21 | Inverter | Central Inverter | All make inverter | Ensure ventilation and colling system of inverter/Inverter room | 21Central Inverter
22 | Inverter | Central Inverter | All make inverter | Replace the identified faulty/damaged part. | 22Central Inverter
23 | Inverter | Central Inverter | All make inverter | Ensure the functionality of the replaced part | 23Central Inverter
24 | Inverter | Central Inverter | All make inverter | Ensure communication ,alarm and events record. | 24Central Inverter
25 | Inverter | Central Inverter | All make inverter | Ensure SMPS voltage | 25Central Inverter
26 | Inverter | Central Inverter | All make inverter | Ensure Grid voltage | 26Central Inverter
27 | Inverter | Central Inverter | All make inverter | Ensure fresh air requirement of inverter room is as per OEM recommendation | 27Central Inverter
28 | Inverter | Central Inverter | All make inverter | Apply glue gun to fix the loose coonector issure in case of repeated occurence. | 28Central Inverter
29 | Inverter | Central Inverter | All make inverter | Ensure IR value of inverter aftre replcement of burnt part. | 29Central Inverter
30 | Inverter | Central Inverter | All make inverter | Ensure cleaning of carbon on cabinet through CRC in case of flashover | 30Central Inverter
31 | Inverter | Central Inverter | All make inverter | Use anti mouse PU foam for sealing | 31Central Inverter
32 | Inverter | Central Inverter | All make inverter | Ensure the software version of programmed PCB in inverter | 32Central Inverter
33 | Inverter | Central Inverter | All make inverter | Ensure the protection parameter and grid parameter as per Grid code | 33Central Inverter
34 | Inverter | Central Inverter | All make inverter | Ensure the connectivity of three phase cable with precharge contactor/AC breaker | 34Central Inverter
35 | Inverter | Central Inverter | All make inverter | Ensure the feedback of all AC/DC contactors and breakers. | 35Central Inverter
36 | Inverter | Central Inverter | Hitachi Inverter | Implementation of acrylic sheet on IGBT stack in Hitachi inverter | 36Central Inverter
37 | Inverter | Central Inverter | Hitachi Inverter | Heater and hygrostat installation in Hitachi inverter. | 37Central Inverter
38 | Inverter | Central Inverter | Sungrow Inverter | IGBT driver board design issue resulting in PDP Protection Failure in Sungrow inverter. Driver boards are to be replaced for the inverter. | 38Central Inverter
39 | Inverter | Central Inverter | Sungrow Inverter | Replacement of AC trip coil which has manufacturing problem | 39Central Inverter
40 | Inverter | Central Inverter | Sungrow Inverter | Ensure the contro supply should be withi a range. | 40Central Inverter
41 | Inverter | Central Inverter | TMEIC inverter | Modification in inverter.Need to add separator sheet on IGBT stack to protect GDA cards and IGBT section | 41Central Inverter
42 | Inverter | Central Inverter | TMEIC inverter | Check fan's operation status by CFM meter and identify the low perfroming fan and replace it and monitorning Inverter cabinet temperature. | 42Central Inverter
43 | Inverter | Central Inverter | TMEIC inverter | Additional cut out behind CPC unit to improve airflow.Observe the feedback by POC. | 43Central Inverter
1 | Inverter | String Inverter | All make inverter | Change the damaged gasket of string inverter. | 1String Inverter
2 | Inverter | String Inverter | All make inverter | Change the paper membrane with SS membrane in string inverter. | 2String Inverter
3 | Inverter | String Inverter | All make inverter | Sealed the cable entry or minor access gape of the inverter. | 3String Inverter
4 | Inverter | String Inverter | All make inverter | Silica gel [Montmorillomite Desiccant, Hygroscopic type] (Do not use dehumidification type) packets to be kept inside inverter | 4String Inverter
5 | Inverter | String Inverter | All make inverter | Spread natural chips pebbles below inverter to prevent grass growth and humidity. | 5String Inverter
6 | Inverter | String Inverter | All make inverter | Use Ant repellent chalk/gel on inverter door and at cable termination. | 6String Inverter
7 | Inverter | String Inverter | All make inverter | Tightness of Earthing Cable for Inverter cabinet‐both end | 7String Inverter
8 | Inverter | String Inverter | All make inverter | Grass level should not be exceeded more than approx. 200mm below string inverter. | 8String Inverter
9 | Inverter | String Inverter | All make inverter | Ensure & Verify DC voltage of all 8 Strings (Vdc) | 9String Inverter
10 | Inverter | String Inverter | All make inverter | Replace the inverter incase of internal burning | 10String Inverter
11 | Inverter | String Inverter | All make inverter | Ensure & Verify Temperature of AC Cable Termination | 11String Inverter
12 | Inverter | String Inverter | All make inverter | Visual inspection of Heat Sink, any dirt or cable touch | 12String Inverter
13 | Inverter | String Inverter | All make inverter | Ensure ventilation and colling system of inverter/Inverter room | 13String Inverter
14 | Inverter | String Inverter | All make inverter | Replace the identified faulty/damaged part. | 14String Inverter
15 | Inverter | String Inverter | All make inverter | Ensure the functionality of the replaced part | 15String Inverter
16 | Inverter | String Inverter | All make inverter | Ensure communication ,alarm and events record. | 16String Inverter
17 | Inverter | String Inverter | All make inverter | Ensure SMPS voltage | 17String Inverter
18 | Inverter | String Inverter | All make inverter | Ensure Grid voltage | 18String Inverter
19 | Inverter | String Inverter | All make inverter | Ensure fresh air requirement of inverter room is as per OEM recommendation | 19String Inverter
20 | Inverter | String Inverter | All make inverter | Ensure the protection parameter and grid parameter as per Grid code | 20String Inverter
1 | LT Panel | LT Panel | ACB | The Healthiness of LV ACB to be ensured for its operation electrically and mechanically. The electrical operation for tripping through Protection release online is suggested to ensure the healthiness of protection keeping all safety norms. | 1LT Panel
2 | LT Panel | LT Panel | Breaker | Ensure IR testing of LT breakers and maintain record of it. | 2LT Panel
3 | LT Panel | LT Panel | Bus bar | Ensure Insulating paint to be applied in LT panel busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 3LT Panel
4 | LT Panel | LT Panel | Bus duct | Ensure silica gel quality of bus duct (NSPBD/SPBD) breather and also ensure breather is sealed properly & breathing process through silica breather only. | 4LT Panel
5 | LT Panel | LT Panel | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 5LT Panel
6 | LT Panel | LT Panel | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 6LT Panel
7 | LT Panel | LT Panel | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 7LT Panel
8 | LT Panel | LT Panel | Cellar | Ensure cable Cellar should be properly sealed. | 8LT Panel
9 | LT Panel | LT Panel | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. | 9LT Panel
10 | LT Panel | LT Panel | Contacts | Ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulfasion observed make record of it and clean with cleaning agent. | 10LT Panel
11 | LT Panel | LT Panel | Control Cable | Ensure control cable casing is tied with cable tie | 11LT Panel
12 | LT Panel | LT Panel | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 12LT Panel
13 | LT Panel | LT Panel | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 13LT Panel
14 | LT Panel | LT Panel | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 14LT Panel
15 | LT Panel | LT Panel | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 15LT Panel
16 | LT Panel | LT Panel | Panel | Ensue availibility of phase segregator sheet inside the panel. | 16LT Panel
17 | LT Panel | LT Panel | Panel | Ensure Gap between two metal plates should be first packed with aluminium plates after that small/minor gaps should be filled with foam and ensure to clean surface properly where ever foam is applied. | 17LT Panel
18 | LT Panel | LT Panel | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. | 18LT Panel
19 | LT Panel | LT Panel | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 19LT Panel
20 | LT Panel | LT Panel | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. | 20LT Panel
1 | ODU | Out door type -A Panel | Battery | Ensure float voltage correction as per the ambient Temperature above 27 deg. C., is to be ensured/ Automated for better battery life as per OEM recommendation. | 1Out door type -A Panel
2 | ODU | Out door type -A Panel | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 2Out door type -A Panel
3 | ODU | Out door type -A Panel | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 3Out door type -A Panel
4 | ODU | Out door type -A Panel | Breaker | Ensure CRM (From Upper bushing to lower bushing with CB in close condition)to be checked after rack in of breaker to ensure proper contact. | 4Out door type -A Panel
5 | ODU | Out door type -A Panel | Breaker | Ensure IR testing of HT breakers and maintain record of it. | 5Out door type -A Panel
6 | ODU | Out door type -A Panel | Bus PT | Ensure proper connection of bus PT with busbar. | 6Out door type -A Panel
7 | ODU | Out door type -A Panel | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 7Out door type -A Panel
8 | ODU | Out door type -A Panel | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 8Out door type -A Panel
9 | ODU | Out door type -A Panel | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 9Out door type -A Panel
10 | ODU | Out door type -A Panel | Cable Support | Ensure Installation of proper cable support. | 10Out door type -A Panel
11 | ODU | Out door type -A Panel | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. Also, ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulphation observed make record of it and clean with cleaning agent. | 11Out door type -A Panel
12 | ODU | Out door type -A Panel | Control Cable | Ensure cable from HT Panel to IDT used for protection tripping is armour cable. | 12Out door type -A Panel
13 | ODU | Out door type -A Panel | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 13Out door type -A Panel
14 | ODU | Out door type -A Panel | Control Cable | Ensure PVC tape to be applied on DC cable lug used for door limit switch or any protection to prevent mal-opeartion due to lug to panel tracking because of moisture ingress or cable insulation failure. | 14Out door type -A Panel
15 | ODU | Out door type -A Panel | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 15Out door type -A Panel
16 | ODU | Out door type -A Panel | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 16Out door type -A Panel
17 | ODU | Out door type -A Panel | CT | Ensure Length of Bolt used for fixing CT on busbar to be matched with hole length. | 17Out door type -A Panel
18 | ODU | Out door type -A Panel | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 18Out door type -A Panel
19 | ODU | Out door type -A Panel | CT | Visually inspect CT secondary and Pig tail connections for any hot spot at CT terminals from Inspection window. | 19Out door type -A Panel
20 | ODU | Out door type -A Panel | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 20Out door type -A Panel
21 | ODU | Out door type -A Panel | Earthing | Ensure proper earthing connection of CT. | 21Out door type -A Panel
22 | ODU | Out door type -A Panel | Earthing | Ensure separate earth pit with two connection strips from panel and also ensure firm connections. | 22Out door type -A Panel
23 | ODU | Out Door Type -A Panel | Hooter | Breaker trip signal, Block communication failure & DC power pack heathiness signal need to be mapped with hooter at MCR. | 23Out Door Type -A Panel
24 | ODU | Out door type -A Panel | LBS | Ensure bypass LBS mechanism with proper cable size/bus bar where ever failure rate is higher. | 24Out door type -A Panel
25 | ODU | Out door type -A Panel | LBS | Ensure LBS tripping to be removed on door interock and Tripping solenoid contact to be removed from all LBS panels. | 25Out door type -A Panel
26 | ODU | Out door type -A Panel | LBS | Ensure proper alignment of LBS contacts & CRM test need to be taken after every operation of LBS | 26Out door type -A Panel
27 | ODU | Out door type -A Panel | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 27Out door type -A Panel
28 | ODU | Out door type -A Panel | Panel | Ensure availibility of phase segregator sheet inside the panel. | 28Out door type -A Panel
29 | ODU | Out door type -A Panel | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 29Out door type -A Panel
30 | ODU | Out door type -A Panel | Panel | Ensure Insulating paint to be applied in HT panel busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 30Out door type -A Panel
31 | ODU | Out door type -A Panel | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 31Out door type -A Panel
32 | ODU | Out door type -A Panel | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 32Out door type -A Panel
33 | ODU | Out door type -A Panel | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 33Out door type -A Panel
34 | ODU | Out door type -A Panel | Panel | Ensure use of hot air blower before charging of panel to remove moisture from panel.(in case of shutdown of 3-4 hours) | 34Out door type -A Panel
35 | ODU | Out door type -A Panel | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 35Out door type -A Panel
36 | ODU | Out door type -A Panel | Panel | All glands should be intact and to be sealed from inside the panel. | 36Out door type -A Panel
37 | ODU | Out door type -A Panel | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 37Out door type -A Panel
38 | ODU | Out door type -A Panel | Relay | Ensure that Under frequency settings of IDT should be disabled | 38Out door type -A Panel
39 | ODU | Out door type -A Panel | SCADA | Ensure DC supervision relay used in power pack non-stored circuit, in which potential-free contact is available and the same to be used at SCADA for knowing the power pack supply failure. | 39Out door type -A Panel
40 | ODU | Out door type -A Panel | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 40Out door type -A Panel
41 | ODU | Out door type -A Panel | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 41Out door type -A Panel
1 | ODU | Out door type -B Panel | Battery | Ensure float voltage correction as per the ambient Temperature above 27 deg. C., is to be ensured/ Automated for better battery life as per OEM recommendation. | 1Out door type -B Panel
2 | ODU | Out door type -B Panel | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 2Out door type -B Panel
3 | ODU | Out door type -B Panel | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 3Out door type -B Panel
4 | ODU | Out door type -B Panel | Breaker | Ensure CRM (From Upper bushing to lower bushing with CB in close condition)to be checked after rack in of breaker to ensure proper contact. | 4Out door type -B Panel
5 | ODU | Out door type -B Panel | Breaker | Ensure IR testing of HT breakers and maintain record of it. | 5Out door type -B Panel
6 | ODU | Out door type -B Panel | Bus PT | Ensure proper connection of bus PT with busbar. | 6Out door type -B Panel
7 | ODU | Out door type -B Panel | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 7Out door type -B Panel
8 | ODU | Out door type -B Panel | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 8Out door type -B Panel
9 | ODU | Out door type -B Panel | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 9Out door type -B Panel
10 | ODU | Out door type -B Panel | Cable Support | Ensure Installation of proper cable support. | 10Out door type -B Panel
11 | ODU | Out door type -B Panel | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. Also, ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulphation observed make record of it and clean with cleaning agent. | 11Out door type -B Panel
12 | ODU | Out door type -B Panel | Control Cable | Ensure cable from HT Panel to IDT used for protection tripping is armour cable. | 12Out door type -B Panel
13 | ODU | Out door type -B Panel | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 13Out door type -B Panel
14 | ODU | Out door type -B Panel | Control Cable | Ensure PVC tape to be applied on DC cable lug used for door limit switch or any protection to prevent mal-opeartion due to lug to panel tracking because of moisture ingress or cable insulation failure. | 14Out door type -B Panel
15 | ODU | Out door type -B Panel | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 15Out door type -B Panel
16 | ODU | Out door type -B Panel | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 16Out door type -B Panel
17 | ODU | Out door type -B Panel | CT | Ensure Length of Bolt used for fixing CT on busbar to be matched with hole length. | 17Out door type -B Panel
18 | ODU | Out door type -B Panel | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 18Out door type -B Panel
19 | ODU | Out door type -B Panel | CT | Visually inspect CT secondary and Pig tail connections for any hot spot at CT terminals from Inspection window. | 19Out door type -B Panel
20 | ODU | Out door type -B Panel | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 20Out door type -B Panel
21 | ODU | Out door type -B Panel | Earthing | Ensure proper earthing connection of CT. | 21Out door type -B Panel
22 | ODU | Out door type -B Panel | Earthing | Ensure separate earth pit with two connection strips from panel and also ensure firm connections. | 22Out door type -B Panel
23 | ODU | Out Door Type -B Panel | Hooter | Breaker trip signal, Block communication failure & DC power pack heathiness signal need to be mapped with hooter at MCR. | 23Out Door Type -B Panel
24 | ODU | Out door type -B Panel | LBS | Ensure bypass LBS mechanism with proper cable size/bus bar where ever failure rate is higher. | 24Out door type -B Panel
25 | ODU | Out door type -B Panel | LBS | Ensure LBS tripping to be removed on door interock and Tripping solenoid contact to be removed from all LBS panels. | 25Out door type -B Panel
26 | ODU | Out door type -B Panel | LBS | Ensure proper alignment of LBS contacts & CRM test need to be taken after every operation of LBS | 26Out door type -B Panel
27 | ODU | Out door type -B Panel | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 27Out door type -B Panel
28 | ODU | Out door type -B Panel | Panel | Ensure availibility of phase segregator sheet inside the panel. | 28Out door type -B Panel
29 | ODU | Out door type -B Panel | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 29Out door type -B Panel
30 | ODU | Out door type -B Panel | Panel | Ensure Insulating paint to be applied in HT panel busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 30Out door type -B Panel
31 | ODU | Out door type -B Panel | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 31Out door type -B Panel
32 | ODU | Out door type -B Panel | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 32Out door type -B Panel
33 | ODU | Out door type -B Panel | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 33Out door type -B Panel
34 | ODU | Out door type -B Panel | Panel | Ensure use of hot air blower before charging of panel to remove moisture from panel.(in case of shutdown of 3-4 hours) | 34Out door type -B Panel
35 | ODU | Out door type -B Panel | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 35Out door type -B Panel
36 | ODU | Out door type -B Panel | Panel | All glands should be intact and to be sealed from inside the panel. | 36Out door type -B Panel
37 | ODU | Out door type -B Panel | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 37Out door type -B Panel
38 | ODU | Out door type -B Panel | Relay | Ensure that Under frequency settings of IDT should be disabled | 38Out door type -B Panel
39 | ODU | Out door type -B Panel | SCADA | Ensure DC supervision relay used in power pack non-stored circuit, in which potential-free contact is available and the same to be used at SCADA for knowing the power pack supply failure. | 39Out door type -B Panel
40 | ODU | Out door type -B Panel | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 40Out door type -B Panel
41 | ODU | Out door type -B Panel | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 41Out door type -B Panel
0 | Power Boost from 2000KW to 2250KW |  | Control Cable | By installing PT100 sensor hardware to monitor the cable temperature and PLC software installation is required to be upgraded from 2000Kw to 2250Kw. | 0
1 | RMU | RMU | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 1RMU
2 | RMU | RMU | Boot kit | Ensure all RMU cable section need to be protected with proper capacity cable boot. | 2RMU
3 | RMU | RMU | Boot kit | Ensure Boot kits used in RMU with proper rating. | 3RMU
4 | RMU | RMU | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 4RMU
5 | RMU | RMU | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 5RMU
6 | RMU | RMU | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 6RMU
7 | RMU | RMU | Cable Support | Ensure Installation of proper cable support. | 7RMU
8 | RMU | RMU | Control Cable | Ensure cable from HT Panel to IDT used for protection tripping is armour cable. | 8RMU
9 | RMU | RMU | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 9RMU
10 | RMU | RMU | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 10RMU
11 | RMU | RMU | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 11RMU
12 | RMU | RMU | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 12RMU
13 | RMU | RMU | Earthing | Ensure proper earthing connection of CT. | 13RMU
14 | RMU | RMU | Earthing | Ensure separate earth pit with two connection strips from panel and also ensure firm connections. | 14RMU
15 | RMU | RMU | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 15RMU
16 | RMU | RMU | HT Cable | Ensure RMU loop cables to be kept in charge condition by keeeping isolated from one end. | 16RMU
17 | RMU | RMU | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 17RMU
18 | RMU | RMU | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 18RMU
19 | RMU | RMU | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 19RMU
20 | RMU | RMU | Panel | Ensure Insulating paint to be applied in cable section to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 20RMU
21 | RMU | RMU | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 21RMU
22 | RMU | RMU | Panel | Ensure use of hot air blower before charging of panel to remove moisture from panel.(in case of shutdown of 3-4 hours) | 22RMU
23 | RMU | RMU | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 23RMU
24 | RMU | RMU | Panel | All glands should be intact and to be sealed from inside the panel. | 24RMU
25 | RMU | RMU | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 25RMU
26 | RMU | RMU | Relay | Ensure that Under frequency settings of IDT should be disabled | 26RMU
27 | RMU | RMU | SCADA | Ensure DC supervision relay used in power pack non-stored circuit, in which potential-free contact is available and the same to be used at SCADA for knowing the power pack supply failure. | 27RMU
28 | RMU | RMU | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 28RMU
1 | SCB/JB/AJB/SMB | SCB/JB/AJB/SMB | All type of SCB | Ensure tightness of Input/output cables | 1SCB/JB/AJB/SMB
2 | SCB/JB/AJB/SMB | SCB/JB/AJB/SMB | All type of SCB | Ensure cleanliness of internal cabinet | 2SCB/JB/AJB/SMB
3 | SCB/JB/AJB/SMB | SCB/JB/AJB/SMB | All type of SCB | Ensure healthiness of communication | 3SCB/JB/AJB/SMB
4 | SCB/JB/AJB/SMB | SCB/JB/AJB/SMB | All type of SCB | Routine thermography of SCB/JB/AJB/SMB | 4SCB/JB/AJB/SMB
1 | Switchgear | Switchboard Aux. Transformer Feeder | Battery | Ensure float voltage correction as per the ambient Temperature above 27 deg. C., is to be ensured/ Automated for better battery life as per OEM recommendation. | 1Switchboard Aux. Transformer Feeder
2 | Switchgear | Switchboard Aux. Transformer Feeder | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 2Switchboard Aux. Transformer Feeder
3 | Switchgear | Switchboard Aux. Transformer Feeder | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 3Switchboard Aux. Transformer Feeder
4 | Switchgear | Switchboard Aux. Transformer Feeder | Breaker | Ensure CRM (From Upper bushing to lower bushing with CB in close condition)to be checked after rack in of breaker to ensure proper contact. | 4Switchboard Aux. Transformer Feeder
5 | Switchgear | Switchboard Aux. Transformer Feeder | Breaker | Ensure IR testing of HT breakers and maintain record of it. | 5Switchboard Aux. Transformer Feeder
6 | Switchgear | Switchboard Aux. Transformer Feeder | Bus PT | Ensure proper connection of bus PT with busbar. | 6Switchboard Aux. Transformer Feeder | 1
7 | Switchgear | Switchboard Aux. Transformer Feeder | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 7Switchboard Aux. Transformer Feeder | 1
8 | Switchgear | Switchboard Aux. Transformer Feeder | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 8Switchboard Aux. Transformer Feeder | 1
9 | Switchgear | Switchboard Aux. Transformer Feeder | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 9Switchboard Aux. Transformer Feeder
10 | Switchgear | Switchboard Aux. Transformer Feeder | Cable Support | Ensure Installation of proper cable support. | 10Switchboard Aux. Transformer Feeder
11 | Switchgear | Switchboard Aux. Transformer Feeder | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. Also, ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulphation observed make record of it and clean with cleaning agent. | 11Switchboard Aux. Transformer Feeder | 1
12 | Switchgear | Switchboard Aux. Transformer Feeder | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 12Switchboard Aux. Transformer Feeder | 1
13 | Switchgear | Switchboard Aux. Transformer Feeder | Control Cable | Ensure PVC tape to be applied on DC cable lug used for door limit switch or any protection to prevent mal-opeartion due to lug to panel tracking because of moisture ingress or cable insulation failure. | 13Switchboard Aux. Transformer Feeder | 1
14 | Switchgear | Switchboard Aux. Transformer Feeder | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 14Switchboard Aux. Transformer Feeder | 1
15 | Switchgear | Switchboard Aux. Transformer Feeder | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 15Switchboard Aux. Transformer Feeder
16 | Switchgear | Switchboard Aux. Transformer Feeder | CT | Ensure Length of Bolt used for fixing CT on busbar to be matched with hole length. | 16Switchboard Aux. Transformer Feeder
17 | Switchgear | Switchboard Aux. Transformer Feeder | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 17Switchboard Aux. Transformer Feeder
18 | Switchgear | Switchboard Aux. Transformer Feeder | CT | Visually inspect CT secondary and Pig tail connections for any hot spot at CT terminals from Inspection window. | 18Switchboard Aux. Transformer Feeder
19 | Switchgear | Switchboard Aux. Transformer Feeder | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 19Switchboard Aux. Transformer Feeder
20 | Switchgear | Switchboard Aux. Transformer Feeder | Earthing | Ensure proper earthing connection of CT. | 20Switchboard Aux. Transformer Feeder
21 | Switchgear | Switchboard Aux. Transformer Feeder | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 21Switchboard Aux. Transformer Feeder
22 | Switchgear | Switchboard Aux. Transformer Feeder | LBS | Ensure bypass LBS mechanism with proper cable size/bus bar where ever failure rate is higher. | 22Switchboard Aux. Transformer Feeder
23 | Switchgear | Switchboard Aux. Transformer Feeder | LBS | Ensure LBS tripping to be removed on door interock and Tripping solenoid contact to be removed from all LBS panels. | 23Switchboard Aux. Transformer Feeder
24 | Switchgear | Switchboard Aux. Transformer Feeder | LBS | Ensure proper alignment of LBS contacts & CRM test need to be taken after every operation of LBS | 24Switchboard Aux. Transformer Feeder
25 | Switchgear | Switchboard Aux. Transformer Feeder | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 25Switchboard Aux. Transformer Feeder
26 | Switchgear | Switchboard Aux. Transformer Feeder | MCR | The switchgear room environment should be maintained dust free and frequency of cleaning should be on quarterly basis. | 26Switchboard Aux. Transformer Feeder
27 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure availibility of phase segregator sheet inside the panel. | 27Switchboard Aux. Transformer Feeder
28 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 28Switchboard Aux. Transformer Feeder
29 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure Insulating paint to be applied in HT panel and busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 29Switchboard Aux. Transformer Feeder
30 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 30Switchboard Aux. Transformer Feeder
31 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 31Switchboard Aux. Transformer Feeder
32 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 32Switchboard Aux. Transformer Feeder | 1
33 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 33Switchboard Aux. Transformer Feeder
34 | Switchgear | Switchboard Aux. Transformer Feeder | Panel | All glands should be intact and to be sealed from inside the panel. | 34Switchboard Aux. Transformer Feeder
35 | Switchgear | Switchboard Aux. Transformer Feeder | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 35Switchboard Aux. Transformer Feeder
36 | Switchgear | Switchboard Aux. Transformer Feeder | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 36Switchboard Aux. Transformer Feeder
37 | Switchgear | Switchboard Aux. Transformer Feeder | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 37Switchboard Aux. Transformer Feeder
1 | Switchgear | Switchboard Bus PT | Bus PT | Ensure proper connection of bus PT with busbar. | 1Switchboard Bus PT
2 | Switchgear | Switchboard Bus PT | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 2Switchboard Bus PT
3 | Switchgear | Switchboard Bus PT | Earthing | Ensure proper earthing connection of PT. | 3Switchboard Bus PT
4 | Switchgear | Switchboard Bus PT | MCR | The switchgear room environment should be maintained dust free and frequency of cleaning should be on quarterly basis. | 4Switchboard Bus PT
5 | Switchgear | Switchboard Bus PT | Panel | Ensure availibility of phase segregator sheet inside the panel, if phase to phase clearance is not as per standards. | 5Switchboard Bus PT
6 | Switchgear | Switchboard Bus PT | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 6Switchboard Bus PT
7 | Switchgear | Switchboard Bus PT | Panel | Ensure Insulating paint to be applied in HT panel and busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 7Switchboard Bus PT
8 | Switchgear | Switchboard Bus PT | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 8Switchboard Bus PT
9 | Switchgear | Switchboard Bus PT | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 9Switchboard Bus PT
10 | Switchgear | Switchboard Bus PT | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 10Switchboard Bus PT
11 | Switchgear | Switchboard Bus PT | Panel | All glands should be intact and to be sealed from inside the panel. | 11Switchboard Bus PT
12 | Switchgear | Switchboard Bus PT | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 12Switchboard Bus PT
13 | Switchgear | Switchboard Bus PT | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 13Switchboard Bus PT
1 | Switchgear | Switchboard Incomer Feeder | Battery | Ensure float voltage correction as per the ambient Temperature above 27 deg. C., is to be ensured/ Automated for better battery life as per OEM recommendation. | 1Switchboard Incomer Feeder
2 | Switchgear | Switchboard Incomer Feeder | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 2Switchboard Incomer Feeder
3 | Switchgear | Switchboard Incomer Feeder | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 3Switchboard Incomer Feeder
4 | Switchgear | Switchboard Incomer Feeder | Breaker | Ensure CRM (From Upper bushing to lower bushing with CB in close condition)to be checked after rack in of breaker to ensure proper contact. | 4Switchboard Incomer Feeder
5 | Switchgear | Switchboard Incomer Feeder | Breaker | Ensure IR testing of HT breakers and maintain record of it. | 5Switchboard Incomer Feeder
6 | Switchgear | Switchboard Incomer Feeder | Bus PT | Ensure proper connection of bus PT with busbar. | 6Switchboard Incomer Feeder
7 | Switchgear | Switchboard Incomer Feeder | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 7Switchboard Incomer Feeder
8 | Switchgear | Switchboard Incomer Feeder | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 8Switchboard Incomer Feeder
9 | Switchgear | Switchboard Incomer Feeder | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 9Switchboard Incomer Feeder
10 | Switchgear | Switchboard Incomer Feeder | Cable Support | Ensure Installation of proper cable support. | 10Switchboard Incomer Feeder
11 | Switchgear | Switchboard Incomer Feeder | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. Also, ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulphation observed make record of it and clean with cleaning agent. | 11Switchboard Incomer Feeder
12 | Switchgear | Switchboard Incomer Feeder | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 12Switchboard Incomer Feeder
13 | Switchgear | Switchboard Incomer Feeder | Control Cable | Ensure PVC tape to be applied on DC cable lug used for door limit switch or any protection to prevent mal-opeartion due to lug to panel tracking because of moisture ingress or cable insulation failure. | 13Switchboard Incomer Feeder
14 | Switchgear | Switchboard Incomer Feeder | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 14Switchboard Incomer Feeder
15 | Switchgear | Switchboard Incomer Feeder | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 15Switchboard Incomer Feeder
16 | Switchgear | Switchboard Incomer Feeder | CT | Ensure Length of Bolt used for fixing CT on busbar to be matched with hole length. | 16Switchboard Incomer Feeder
17 | Switchgear | Switchboard Incomer Feeder | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 17Switchboard Incomer Feeder
18 | Switchgear | Switchboard Incomer Feeder | CT | Visually inspect CT secondary and Pig tail connections for any hot spot at CT terminals from Inspection window. | 18Switchboard Incomer Feeder
19 | Switchgear | Switchboard Incomer Feeder | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 19Switchboard Incomer Feeder
20 | Switchgear | Switchboard Incomer Feeder | Earthing | Ensure proper earthing connection of CT. | 20Switchboard Incomer Feeder
21 | Switchgear | Switchboard Incomer Feeder | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 21Switchboard Incomer Feeder
22 | Switchgear | Switchboard Incomer Feeder | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 22Switchboard Incomer Feeder
23 | Switchgear | Switchboard Incomer Feeder | MCR | The switchgear room environment should be maintained dust free and frequency of cleaning should be on quarterly basis. | 23Switchboard Incomer Feeder
24 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure availibility of phase segregator sheet inside the panel. | 24Switchboard Incomer Feeder
25 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 25Switchboard Incomer Feeder
26 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure Insulating paint to be applied in HT panel and busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 26Switchboard Incomer Feeder
27 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 27Switchboard Incomer Feeder
28 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 28Switchboard Incomer Feeder
29 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 29Switchboard Incomer Feeder
30 | Switchgear | Switchboard Incomer Feeder | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 30Switchboard Incomer Feeder
31 | Switchgear | Switchboard Incomer Feeder | Panel | All glands should be intact and to be sealed from inside the panel. | 31Switchboard Incomer Feeder
32 | Switchgear | Switchboard Incomer Feeder | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 32Switchboard Incomer Feeder
33 | Switchgear | Switchboard Incomer Feeder | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 33Switchboard Incomer Feeder
34 | Switchgear | Switchboard Incomer Feeder | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 34Switchboard Incomer Feeder
1 | Switchgear | Switchboard Outgoing feeder | Battery | Ensure float voltage correction as per the ambient Temperature above 27 deg. C., is to be ensured/ Automated for better battery life as per OEM recommendation. | 1Switchboard Outgoing feeder
2 | Switchgear | Switchboard Outgoing feeder | Battery | Ensure healthiness of powerpack batteries by taking load on battery with incoming supply OFF, if found faulty replace. and ensure DC Control supply Healthiness. | 2Switchboard Outgoing feeder
3 | Switchgear | Switchboard Outgoing feeder | Breaker | Ensure circuit breakers need to operated for OPEN and CLOSE with AC control supply available and for TRIP without AC control supply condition. | 3Switchboard Outgoing feeder
4 | Switchgear | Switchboard Outgoing feeder | Breaker | Ensure CRM (From Upper bushing to lower bushing with CB in close condition)to be checked after rack in of breaker to ensure proper contact. | 4Switchboard Outgoing feeder
5 | Switchgear | Switchboard Outgoing feeder | Breaker | Ensure IR testing of HT breakers and maintain record of it. | 5Switchboard Outgoing feeder
6 | Switchgear | Switchboard Outgoing feeder | Bus duct | Ensure silica gel quality of bus duct (NSPBD/SPBD) breather and also ensure breather is sealed properly & breathing process through silica breather only. | 6Switchboard Outgoing feeder
7 | Switchgear | Switchboard Outgoing feeder | Bus PT | Ensure proper connection of bus PT with busbar. | 7Switchboard Outgoing feeder
8 | Switchgear | Switchboard Outgoing feeder | Busbar | Ensure High quality nut & bolts to be used in cables & busbar connection. Also, ensure rusted lugs, nuts are to be replaced with new one. | 8Switchboard Outgoing feeder
9 | Switchgear | Switchboard Outgoing feeder | Busbar | Ensure HT tape to be applied on bare busbar. And also on busbar joint section before using old insulation shroud after fault. | 9Switchboard Outgoing feeder
10 | Switchgear | Switchboard Outgoing feeder | Busbar | Ensure there is no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque on hardware (Ensure assembly fitments), else it may lead to a higher temperature rise. | 10Switchboard Outgoing feeder
11 | Switchgear | Switchboard Outgoing feeder | Cable Support | Ensure Installation of proper cable support. | 11Switchboard Outgoing feeder
12 | Switchgear | Switchboard Outgoing feeder | Contacts | Ensure alignment and tulip contact discoloring of male-female contacts of circuit breaker to be checked during maintenance. Also, ensure breaker male-female contacts to be cleaned properly in routine maintenance and if sulphation observed make record of it and clean with cleaning agent. | 12Switchboard Outgoing feeder
13 | Switchgear | Switchboard Outgoing feeder | Control Cable | Ensure healthiness of Power & Control cables by checking IR values. Also, Ensure Control/Power Cable healthiness near gland area, there must not be any damages. If required, conduit pipe to be used to protect control cable againts sharp edges. | 13Switchboard Outgoing feeder
14 | Switchgear | Switchboard Outgoing feeder | Control Cable | Ensure PVC tape to be applied on DC cable lug used for door limit switch or any protection to prevent mal-opeartion due to lug to panel tracking because of moisture ingress or cable insulation failure. | 14Switchboard Outgoing feeder
15 | Switchgear | Switchboard Outgoing feeder | Control Cable | Ensure routing of control cable should be properly separated from power cable. | 15Switchboard Outgoing feeder
16 | Switchgear | Switchboard Outgoing feeder | Control Cable | Measure Loop resistance and IR of CT secondary circuit and record. | 16Switchboard Outgoing feeder
17 | Switchgear | Switchboard Outgoing feeder | CT | Ensure Length of Bolt used for fixing CT on busbar to be matched with hole length. | 17Switchboard Outgoing feeder
18 | Switchgear | Switchboard Outgoing feeder | CT | Ensure Physical Inspection & tightness of busbar and CT's to be done every Quarterly basis. | 18Switchboard Outgoing feeder
19 | Switchgear | Switchboard Outgoing feeder | CT | Visually inspect CT secondary and Pig tail connections for any hot spot at CT terminals from Inspection window. | 19Switchboard Outgoing feeder
20 | Switchgear | Switchboard Outgoing feeder | Earthing | Ensure earthing connection tightness and record earthing values with grid & without grid and necessary actions to be taken if found abnormal. Also, If earthing bus is provided in panel then earthing should be done at 2-3 locations across length. | 20Switchboard Outgoing feeder
21 | Switchgear | Switchboard Outgoing feeder | Earthing | Ensure proper earthing connection of CT. | 21Switchboard Outgoing feeder
22 | Switchgear | Switchboard Outgoing Feeder | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 22Switchboard Outgoing Feeder
23 | Switchgear | Switchboard Outgoing feeder | Limit Switch | Ensure proper functioning of door limit switch as per scheme drawing to be checked. | 23Switchboard Outgoing feeder
24 | Switchgear | Switchboard Outgoing feeder | MCR | The switchgear room environment should be maintained dust free and frequency of cleaning should be on quarterly basis. | 24Switchboard Outgoing feeder
25 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure availibility of phase segregator sheet inside the panel. | 25Switchboard Outgoing feeder
26 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure cleaning of total panel including insulators, LA and other surroundings on quarterly basis. | 26Switchboard Outgoing feeder
27 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure Insulating paint to be applied in HT panel and busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 27Switchboard Outgoing feeder
28 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure Panel testing data to be compared with FAT and Commissioning data. | 28Switchboard Outgoing feeder
29 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure Proper sealing of all panels to ensure IP55 protection. with door gaskets, cable entries and proper alignment of doors. Also, ensure cable Cellar associated with panel should be properly sealed. | 29Switchboard Outgoing feeder
30 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure Silica gel bag/Vapor capsule to be placed inside panel to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 30Switchboard Outgoing feeder
31 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure use of hot air blower before charging of panel to remove moisture from panel.(in case of shutdown of 3-4 hours) | 31Switchboard Outgoing feeder
32 | Switchgear | Switchboard Outgoing feeder | Panel | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 32Switchboard Outgoing feeder
33 | Switchgear | Switchboard Outgoing feeder | Panel | All glands should be intact and to be sealed from inside the panel. | 33Switchboard Outgoing feeder
34 | Switchgear | Switchboard Outgoing feeder | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 34Switchboard Outgoing feeder
35 | Switchgear | Switchboard Outgoing feeder | Space heater | Ensure adequate capacity & functioning of space heater and same to be increased if required also check panel heater position for proper Heating. Also, Panel heater position to be ensured that should not be in direct touch/contact with near by cables. If required, blower type heater to be placed where high humidity observed inside the panel. | 35Switchboard Outgoing feeder
36 | Switchgear | Switchboard Outgoing feeder | Surge Arrester | Need to take IR values of Surge/Lightning Arrestor in pre-monsoon and post-monsoon activity. | 36Switchboard Outgoing feeder
1 | Switchyard | Power Transformer | Bus duct | Ensure silica gel quality of bus duct (NSPBD/SPBD) breather and also ensure breather is sealed properly & breathing process through silica breather only. | 1Power Transformer
2 | Switchyard | Power Transformer | Busbar | Ensure additional support to be provided to LV Busbar from top side if existing support is not adequate. Also, ensure Installation of proper cable support at HV side if applicable. | 2Power Transformer
3 | Switchyard | Power Transformer | Busbar | Ensure Bimetallic strip to be used where copper and aluminum are connected with each other, and Stainless steel bolt must be used for connection if existing found corroded. | 3Power Transformer
4 | Switchyard | Power Transformer | Cable box | Ensure during checking of cable box, if any insulator found over heated, cracked or miss aligned must be replaced with new one. | 4Power Transformer
5 | Switchyard | Power Transformer | Cable Box | Ensure Insulating paint to be applied in HV & LV Cable box busbar to provide additional insulation. And ensure proper use of Insulation paint where ever carbon is spread due to flashover inside panel. | 5Power Transformer
6 | Switchyard | Power Transformer | Cable box | Ensure no gap between busbar surface and cable lug. It must be in full contact with busbar surface. Apply recommended torque to ensure assembly fitments. | 6Power Transformer
7 | Switchyard | Power Transformer | Cable box | Ensure Phase to Phase separation sheet to be used where ever phase to phase clearance is not as per standerd in transformer hv and lv side. | 7Power Transformer
8 | Switchyard | Power Transformer | Cable box | Ensure Proper sealing of all cable box to ensure IP protection with door gaskets and cable entries. | 8Power Transformer
9 | Switchyard | Power Transformer | Cable box | Ensure Silica gel bag/Vapor capsule to be placed inside cable box to control moisture level. Frequency of Visual inspection to check healthiness of silica gel to be increased as per the actual site condition. | 9Power Transformer
10 | Switchyard | Power Transformer | Cable box | Ensure thermography of LV box to be done quarterly and need to be compare with other IDT. | 10Power Transformer
11 | Switchyard | Power Transformer | Cable box | Ensure Use of moisture removal spray(8070 ELECTRICAL 88 CO2 HIGH FLOW SHP 360) on all surfaces of bus, insulators, cable terminations etc. | 11Power Transformer
12 | Switchyard | Power Transformer | Cable tray | Ensure LV cables to be properly laid on cable tray with trefoil formation and distance between trefoil to be maintain to avoid induction and leakage current. Also, ensure & check effective earthing of cable trays throughout the length. | 12Power Transformer
13 | Switchyard | Power Transformer | Control Cable | Ensure cable are having proper cable glands at cable entry point of Buchholz, PRV and MOG. | 13Power Transformer
14 | Switchyard | Power Transformer | Control Cable | Ensure cable from Power transformer to Transformer control & protection panel used for protection tripping is armour cable. | 14Power Transformer
15 | Switchyard | Power Transformer | Control Cable | Validate IR value of relay contacts and control cables used for protection (PRV, MOG, Buchholz, WTI, OTI etc.) also ensure tightness of Control cable connections and provide record. Also, verify PRV and Bucholz relay switch rating with its name plate details. | 15Power Transformer
16 | Switchyard | Power Transformer | Earthing | Ensure effective earthing of Neutral point of ICT at PSS end. | 16Power Transformer
17 | Switchyard | Power Transformer | Earthing | Ensure healthiness of earthing resistance measurement and maintain record. | 17Power Transformer
18 | Switchyard | Power Transformer | Hooter | All alarm & trip signal need to be mapped with hooter at MCR. | 18Power Transformer
19 | Switchyard | Power Transformer | Junction box | Ensure Magic gel application at all JBs (Side-mounted PRV of JB,Buchholz,etc), and need to perform protection simulation of PRV & Buchholz through actual operation after application of magic gel & before charging. | 19Power Transformer
20 | Switchyard | Power Transformer | Mechanical Protection | Ensure and verify mechanical protection (WTI, OTI, PRV, Buchholz, MOG, OSR etc.) simulation at Filed/Local panel & at SCADA. Also, verify SCADA data for reporting of alarms & trippings | 20Power Transformer
21 | Switchyard | Power transformer | NIFPS | Ensure Transformer NIFPS NRV/TCIV valve handle tied with cable tie or locked in service position. | 21Power transformer
22 | Switchyard | Power Transformer | Oil | Ensure oil spillage to be cleared immediately from all the affected areas during oil top-up activity and while releasing air from transformer, | 22Power Transformer
23 | Switchyard | Power Transformer | Oil | Oil level in transformer should be between 30 deg. & ½ indication in Magnetic Oil Gauge(MOG) when the ambient temperature is 30 deg. Celsius. | 23Power Transformer
24 | Switchyard | Power Transformer | OTI-WTI | Ensure healthiness of WTI & OTI transducer and verify temperature readings at Local and in SCADA. | 24Power Transformer
25 | Switchyard | Power Transformer | OTI-WTI | Ensure WTI-OTI settings must be as per OEM recomendation. | 25Power Transformer
26 | Switchyard | Power Transformer | Power cable | Ensure healthiness of Power cables by checking IR values. | 26Power Transformer
27 | Switchyard | Power Transformer | Power Transformer | Ensure any deposition of oil & dust over Junction Box, Cable box and over tank surface to be properly cleaned. | 27Power Transformer
28 | Switchyard | Power Transformer | Power Transformer | Transformer routine test to be performed and test results to be matched with FAT report. | 28Power Transformer
29 | Switchyard | Power Transformer | Terminal Box | Ensure application of Magic gel at all JBs (PRV,Buchholz,etc) | 29Power Transformer
30 | Switchyard | Power Transformer | Valve | Ensure apply lock on oil drain valve of IDT to prevent oil theft where ever oil theft cases observed. | 30Power Transformer
1 | Switchyard | Switchyard Equipment | Breaker | IR testing of HT breakers to be done | 1Switchyard Equipment
2 | Switchyard | Switchyard Equipment | Connector | Ensure clamp connectors tightening with proper torque suggested by OEM. | 2Switchyard Equipment
3 | Switchyard | Switchyard Equipment | Control cable | Ensure healthiness of CT secondary circuit by having loop resistance and Insulation resistance and maintain record of it. | 3Switchyard Equipment
4 | Switchyard | Switchyard Equipment | Isolator | Ensure isolator healthiness by checking contact resistance measurement & Thermography after every isolator operation. | 4Switchyard Equipment
5 | Switchyard | Switchyard Equipment | LA | Ensure recommended torque applied for jumper connection tightness with LA and ACSR conductor.. | 5Switchyard Equipment
6 | Switchyard | Switchyard Equipment | LA | Earthing values of all LA to be monitor and if earthing resistance value is >1 ohm additional earth pit need to be constructed. Maintain record of earth pit resistance value. | 6Switchyard Equipment
7 | Switchyard | Switchyard Equipment | LA | Ensure proper earthing continuity between LA and its earth pit. | 7Switchyard Equipment
8 | Switchyard | Switchyard Equipment | LA | Ensure separate riser connection (Earthing strip) to be install/run from LA to earthing pit with minimum no's of joints. | 8Switchyard Equipment
9 | Switchyard | Switchyard Equipment | LA | Ensure LA mounting to be removed where LA counter is not installed. | 9Switchyard Equipment
10 | Switchyard | Switchyard Equipment | LA | Ensure testing of LA counter and leakage current(mA) to be done on yearly/opportunity outage basis. | 10Switchyard Equipment
11 | Switchyard | Switchyard Equipment | LA | Ensure porcelain type LA to be replaced with polymeric type where failure rate higher in internal transmission line.. | 11Switchyard Equipment
12 | Switchyard | Switchyard Equipment | LA | Ensure Sealing of Outdoor-LA top cover with silicon sealant to prevent moisture ingress. | 12Switchyard Equipment
13 | Switchyard | Switchyard Equipment | LA | Ensure IR values of LA, monitor leakage current and record counters as per ENDORSE-SMP and take necessary actions. | 13Switchyard Equipment
14 | Switchyard | Switchyard Equipment | LA | Ensure to inspect LA visually If any cracks/deformation observed at base and top plate LAs IS to be replaced. | 14Switchyard Equipment
15 | Switchyard | Switchyard Equipment | LA | Ensure IR values of LA, monitor leakage current and record counters as per ENDORSE-SMP and take necessary actions. | 15Switchyard Equipment
16 | Switchyard | Switchyard Equipment | LA | Ensure to inspect LA visually If any cracks/deformation observed at base and top plate LAs IS to be replaced. | 16Switchyard Equipment
17 | Switchyard | Switchyard Equipment | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 17Switchyard Equipment
18 | Switchyard | Switchyard Equipment | Relay | Ensure DR should be enabled in every relay. Time synchronizing of all relays and control devices to be ensured with GPS. In case of unavailability of GPS, manual time clock setting of all devices to be ensured regularly and recorded. | 18Switchyard Equipment
19 | Switchyard | Switchyard Equipment | Switchyard Equipment | Ensure healthiness of earthing resistance measurement of all switchyard equipment's (LA, Wave trap, CT, PT, Isolator, Breaker, BPI etc.) and maintain record. | 19Switchyard Equipment
20 | Switchyard | Switchyard Equipment | Switchyard Equipment | Thermography of all switchyard equipment to be carried out on quarterly basis and necessary corrective actions to be taken if temperature increases than permissible limits allowed in standards. | 20Switchyard Equipment
21 | Switchyard | Switchyard Equipment | Switchyard Equipment | Ensure healthiness of earthing resistance measurement of all switchyard equipment's (LA, Wave trap, CT, PT, Isolator, Breaker, BPI etc.) and maintain record. | 21Switchyard Equipment
22 | Switchyard | Switchyard Equipment | Switchyard Equipment | Thermography of all switchyard equipment to be carried out on quarterly basis and necessary corrective actions to be taken if temperature increases than permissible limits allowed in standards. | 22Switchyard Equipment
23 | Switchyard | Switchyard Equipment | Transmission line | Ensure periodic inspection of transmission line and substation with binocular. | 23Switchyard Equipment
24 | Switchyard | Switchyard Equipment | Transmission line | Ensure clearance between transmission line conductor and earth wire as per applicable standard. Also ensure proper binding & twisting of earth wire on tower with no rusting at the contact area. | 24Switchyard Equipment
25 | Switchyard | Switchyard Equipment | Transmission line | Ensure periodic inspection of transmission line and substation with binocular. | 25Switchyard Equipment
1 | Tracker | Tracker | Control Cable | Maintain proper cable dressing to prevent damage of Motor to SPC cable | 1Tracker
2 | Tracker | Tracker | Control Cable | Partially damaged SPC Anteena will be replaced by inhouse team and Fully damaged will be replaced by new one. | 2Tracker
3 | Tracker | Tracker | Control Cable | Maintain proper cable dressing to prevent damage of Motor to SPC cable | 3Tracker
4 | Tracker | Tracker | Control Cable | Partially damaged SPC Anteena will be replaced by inhouse team and Fully damaged will be replaced by new one. | 4Tracker
5 | Tracker | Tracker | Control Cable | Maintain proper cable dressing to prevent damage of Motor to SPC cable | 5Tracker
6 | Tracker | Tracker | Control Cable | Partially damaged SPC Anteena will be replaced by inhouse team and Fully damaged will be replaced by new one. | 6Tracker
7 | Tracker | Tracker | Cotrol box | Replace the faulty/damaged parts | 7Tracker
8 | Tracker | Tracker | Cotrol box | Ensure the communication of tracke with SCADA | 8Tracker
9 | Tracker | Tracker | Cotrol box | Replace the limit switch | 9Tracker
10 | Tracker | Tracker | Cotrol box | Ensure the status of tilt sensor | 10Tracker
11 | Tracker | Tracker | Cotrol box | Replace the faulty/damaged parts | 11Tracker
12 | Tracker | Tracker | Cotrol box | Ensure the communication of tracke with SCADA | 12Tracker
13 | Tracker | Tracker | Cotrol box | Replace the limit switch | 13Tracker
14 | Tracker | Tracker | Cotrol box | Ensure the status of tilt sensor | 14Tracker
15 | Tracker | Tracker | MMS | Internal tracker to be converted in extrier tracker for Nextracker | 15Tracker
16 | Tracker | Tracker | MMS | Internal tracker to be converted in extrier tracker for Nextracker | 16Tracker
1 | USS | USS | Control Cable | 1) Control and Relay panel door should be proper locked 2) MOG alarm to be incorporated in tripping circuit | 1USS
2 | USS | USS | Control Cable | All WTG cable need to check for trifall | 2USS
3 | USS | USS | Control Cable | DO fuse to be replaced and fixed as per standard procedure in all Ice cube make HT yard structure. | 3USS
0 | USS |  | Control Cable | 1) Control and Relay panel door should be proper locked 2) MOG alarm to be incorporated in tripping circuit | 0
0 | USS |  | Control Cable | All WTG cable need to check for trifall | 0
0 | USS |  | Control Cable | DO fuse to be replaced and fixed as per standard procedure in all Ice cube make HT yard structure. | 0
1 | WMS | WMS | All type of WMS | Ensure SPD healthiness | 1WMS
2 | WMS | WMS | All type of WMS | signal cable should not be laid within power cable trench | 2WMS
3 | WMS | WMS | All type of WMS | Lightning arrester shoul be installed. | 3WMS
4 | WMS | WMS | All type of WMS | Ensure SPD healthiness | 4WMS
5 | WMS | WMS | All type of WMS | signal cable should not be laid within power cable trench | 5WMS
6 | WMS | WMS | All type of WMS | Lightning arrester shoul be installed. | 6WMS
1 | WTG | WTG | Control Cable | Earthing strengthening earthing treatment work initiated | 1WTG
0 | WTG |  | Control Cable | Earthing strengthening earthing treatment work initiated | 0
1 | WTG Power Converter | WTG Power Converter | Control Cable | 1.Common Mode Mitigation Solution (EMI filters Kit) 2.Converter Isolation robust kit In addition to above technical solutions, AMSC also suggested one checklist and the antifrozen coolent % uses. | 1WTG Power Converter
0 | WTG Power Converter |  | Control Cable | 1.Common Mode Mitigation Solution (EMI filters Kit) 2.Converter Isolation robust kit In addition to above technical solutions, AMSC also suggested one checklist and the antifrozen coolent % uses. | 0

## Sheet3-R3 (hidden)
#REF!
PLANT_1 | AREA | SECTION | EQUIPMENT | EQUIPMENT
Bagewadi | MCR | SWITCHYARD | Transmission Line | Transmission Line | 1:00
Bayadgi | SWITCHYARD | SWITCHGEAR | Power Transformer | Power Transformer
Bhadla | BLOCK_1 | RMU/ODU | Switchyard Equipment | Switchyard Equipment |  | SWITCHYARD |  |  | MCR | BLOCK-1 | BLOCK-2 | BLOCK-3 | BLOCK-4 | BLOCK-5 | BLOCK-6 | BLOCK-7 | BLOCK-8 | BLOCK-9 | BLOCK-10 | BLOCK-11 | BLOCK-12 | BLOCK-13 | BLOCK-14 | BLOCK-15 | BLOCK-16 | BLOCK-17 | BLOCK-18 | BLOCK-19 | BLOCK-20 | BLOCK-21 | BLOCK-22 | BLOCK-23 | BLOCK-24 | BLOCK-25 | BLOCK-26 | BLOCK-27 | BLOCK-28 | BLOCK-29 | BLOCK-30 | BLOCK-31 | BLOCK-32 | BLOCK-33 | BLOCK-34 | BLOCK-35 | BLOCK-36 | BLOCK-37 | BLOCK-38 | BLOCK-39 | BLOCK-40 | BLOCK-41 | BLOCK-42 | BLOCK-43 | BLOCK-44
Bitta | BLOCK_2 | LT PANEL | Switchboard Outgoing Feeder | Switchboard Outgoing Feeder |  | SF6 CB |  |  | INCOMER PANEL | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU | RMU/ODU
Channapatna | BLOCK_3 | MCCB | Switchboard Incomer Feeder | Switchboard Incomer Feeder |  | ISOLATOR |  |  | OUTGOING PANEL | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT | IDT
Chattisgarh-01 | BLOCK_4 | IDT | Switchboard Aux. Transformer Feeder | Switchboard Aux. Transformer Feeder |  | PT |  |  | SPARE PANEL | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS | LBS
Chattisgarh-02 | BLOCK_5 | CABLE-ASB TO LT PANEL | Switchboard Bus PT | Switchboard Bus PT |  | CT |  |  | BUS COUPLER | CABLE(FROM RMU/ODU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT) | CABLE(FROM RMU TO IDT)
Ghani | BLOCK_6 | BUSDUCT | RMU | RMU |  | CVT |  |  | LINE PT | LT_PANEL_1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1 | LT PANEL-1
Gubbi | BLOCK_7 | CABLE-IDT TO RMU/ODU | Out Door Type -A Panel | Out Door Type -A Panel |  | LA |  |  | BUS PT | LT_PANEL_2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2 | LT PANEL-2
H Narshipura | BLOCK_8 | CABLE-RMU/ODU TO SWITCHGEAR(MCR) | Out Door Type -B Panel | Out Door Type -B Panel |  | BUS POST INSULATOR(BPI) |  |  | AUX TRAFO | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT | BUSDUCT
Jevargi | BLOCK_9 |  | IDT | IDT |  | BUSBAR |  |  | C&R PANEL | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU) | CABLE(FROM MCR TO RMU/ODU)
Jhansi | BLOCK_10 |  | LT Panel | LT Panel |  | INSULATORS |  |  | BATTERY BANK
Kallur- 10 MW | BLOCK_11 |  | Inverter | MCCB/ACSB |  | JUMPERS |  |  | RTCC PANEL
Kallur- 40 MW | BLOCK_12 |  | Tracker | Bus Duct |  | CLAMP AND CONNECTORS |  |  | METERING PANEL
Kamuthi-AGETL | BLOCK_13 |  | Module & string | String Inverter |  | WAVE TRAP |  |  | DISTRIBUTION BOARD(AC/DC)
Kamuthi-KREL | BLOCK_14 |  | LT Cable | Central Inverter |  | POWER TRANSFORMER |  |  | UPS SYSTEM | LT PANEL-1 | LT PANEL-2 |  | ACSB | MCCB
Kamuthi-KSPL | BLOCK_15 |  | HT Cable | Tracker |  | TRANSMISSION LINE |  |  | BATTERY CHARGER | ACB | ACB |  | INVERTER | CABLE(FROM ACSB TO MCCB)
Kamuthi-RREL | BLOCK_16 |  | Internal Transmission line | WMS |  | NIFPS SYSTEM |  |  | PLCC PANEL | MCCB | MCCB |  | STRING
Kamuthi-RSPL | BLOCK_17 |  | SCADA | SCB/JB/AJB/SMB |  | METERING PANEL |  |  | PLC/SCADA SYSTEM | ACSB | ACSB |  | MODULE
Kanasar | BLOCK_18 |  | Fire | DC Cable |  | OTHER |  |  | FIRE ALARM SYSTEM |  |  |  | CABLE(FROM INVERTER TO ACSB)
Kilaj | BLOCK_19 |  | Theft | LT Cable |  |  |  |  | OTHERS
KR Pete | BLOCK_20 |  | Any other incident cause of property Damage | HT Cable
Maluru | BLOCK_21 |  |  | Internal Transmission Line
Madhuvanhalli-1 | BLOCK_22 |  |  | SCADA
Madhuvanhalli-2 | BLOCK_23 |  |  | Fire
Magadi | BLOCK_24 |  |  | Theft
Mahoba | BLOCK_25 |  |  | Any other incident cause of property Damage
Maskal | BLOCK_26
Nalwar | BLOCK_27
Pavagada-1 | BLOCK_28
Pavagada-2 | BLOCK_29
Pavagada-3 | BLOCK_30
PDPL-01 | BLOCK_31
PDPL-02 | BLOCK_32
Periyapatna | BLOCK_33
Rajeshwar | BLOCK_34
Ramanagara | BLOCK_35
Rastapur | BLOCK_36
Rawra | BLOCK_37
Shorapur | BLOCK_38
T Narsipura | BLOCK_39
TEL OPEN | BLOCK_40
Telangana DCR | BLOCK_41
Tiptur | BLOCK_42
Yatnal | BLOCK_43
BLOCK_44
OTHERS
| Equipment_Category | Switchyard_A | Switchgear_A | RMU_A | ODU_A | IDT_A | HT CABLE | Internal transmission line | LT Panel_MCCB_ACSB_A | AC LT Cable | Inverter_SCB_Module
| Switchyard | Bus Post Insulator (BPI) Issue | Breaker-Internal/Mechanism fault | Control Cable/Auxiliary Circuit Issue | Breaker-internal/Mechanism fault | Buchholz Trip (Transformer Internal fault) | End termination failure at I/C feeder | Line-Conductor Failure | ACB-Contact issue | String Inverter to Field side ASB | Cable fault between inverter and SCB
| Switchgear | Busbar Issue | Breaker-Male & Female Contact Alignment/Failure | CT Control Wiring Issue | Breaker-Male & Female Contact Alignment/Failure | Cable Chamber Flashover | End termination failure at I/C feeder end | Line-Electrocution (Bird, Snake, Monkey etc.) | ACB-CT failure | Field side ASB to LT Panel | Inverter fault
| RMU | Clamp & Connectors Issue | Breaker-Vacuum Bottle Failure | CT Failure | Breaker-Vacuum Bottle Failure | Control Circuit Issue | End termination failure at IDT end | Line-Insulator Failure | ACB-Flashover | String Inverter to LT Panel | SCB fault
| ODU | CT Failure | Busbar Cabinet Issue | False Trip (SCADA, Interlock mall functioning) | Busbar-Melting issue | HV bushing failure | End termination failure at ODU end | Line-Jumper Issue | ACB-Internal Fault | Central Inverter to IDT | String cable fault
| IDT | CVT/PT Failure | Control Cable/Auxiliary Circuit Issue | Flashover (Snake, Rat, Lizard etc.) | Busbar-Shroud Issue | HV Bushing Oil Leakage | End termination failure at OG feeder end | Line-LA Failure | ACB-Malfunction | Other | Other
| LT_Panel_MCCB_ACSB | Isolator Issue | CT Failure | LBS Failure | Control Cable/Auxiliary Circuit Issue | LV bushing failure | End termination failure at Power Transformer end | Line-PG Clamp Melting | Busduct fault
| AC_LT_CABLE | Jumper/Insulator string issue | CT Secondary Wiring Issue | Panel-Moisture ingress | CT Control Wiring Issue | LV Bushing Oil Leakage | End termination failure at RMU end | Line-Tree Touching | Control Cable/Auxiliary Circuit Issue
| HT_CABLE | LA Failure | False Trip (SCADA, Interlock mal functioning) | Power Pack/Aux Supply Issue | CT Failure | MOG AirCell Issue | End termination failure at RMU/ODU end | Other | Flexible Link Issue
| Internal_transmission_line | Line-Tree Touching or Electrocution (Bird, Snake, Monkey etc.) | Flashover-Panel (Moisture, Snake, Rat, Lizard etc.) | Relay-Malfunctioning | False Trip (SCADA, Interlock mal functioning) | NIFPS Issue (Oil drained) | Fault between I/C and ODU |  | MCCB-Flashover
| Inverter_SCB_Module | Malfunctioning (PRV/MOG/Buchholz/WTI/OTI) | LBS Fuse Failure | RMU-Bushing Failure | Flashover (Snake, Rat, Lizard etc.) | NIFPS maloperation | Fault between I/C and RMU |  | MCCB-Internal Fault
| OTHER | False Trip (SCADA, Interlock mal functioning) | LBS issue | RMU-internal/Mechanism Fault | LBS Failure | Oil Leakage Issue (Filtered Oil available) | Fault between IDT and RMU/ODU |  | MCCB-Malfunction
|  | NIFPS Issue (Oil drained) | Manual Trip | RMU-SF6 Gas Leakage | Panel-Moisture ingress | Oil Leakage Issue (Filtration required) | Fault in block to block loop cable(RMU to RMU) |  | MCCB-Thermal Trip
|  | NIFPS maloperation | PT Failure | Other | Panel-Support Insulator Failure | OTI Trip (actual) | Fault in block to block loop cable(ODU to ODU) |  | Nut bolt Looseness/Rusting (Busbar/MCCB)
|  | Power Transformer Internal fault | PT Fuse Failure |  | Power Pack/Aux Supply Issue | OTI Trip (Transformer Internal fault) | Fault between OG feeder and Power transformer |  | Overcurrent/Overload
|  | SF6 CB gas leakage Issue | Relay-Malfunctioning/Setting Issue |  | PT Failure | PRV Trip (Transformer Internal fault) | RMU-Boot Kit Failure |  | Panel-Moisture ingress
|  | SF6 CB pole insulator broken (Main contact) | Tripping coil/Closing coil issue |  | PT Fuse Failure | Malfunctioning (PRV/MOG/Buchholz/WTI/OTI) | Other |  | Other | Other
|  | SF6 CB operating mechanism box/internal issue | Surge Arresster |  | Relay-Malfunctioning | WTI Trip (actual)
|  | Transmission Line Conductor/Cable Fault | Other |  | Surge Arrester | WTI Trip (Transformer Internal fault)
|  | Wave Trap Issue |  |  | Other | WTI-OTI-Capillary Tube Failure
|  | OTHER |  |  |  | Other

## Annexure-1
Sr No | COMMENTS | IMAGE/Link
1 | Supporting images for fault
2 | Images of indication/alarm in SCADA, annunciator, Relay
3 | Equipment drawing
4 | Relay settings (Actual)
5 | DR files of all breakers, tripped during this fault
6 | SCADA event log
7 | Fault history of breakdowns at same location
8 | Last PM checklist
9 | Voltage, Current & Power 1 min. SCADA log
10 | Testing reports of failed equipment
11 | Make & specifications of equipment under breakdown
12 | HT cable fault form